## Slide 1: Repair Kopitiam Specialty Electrical Equipment
By: Yeo Kheng Meng (yeokm1@gmail.com)
http://yeokhengmeng.com/2016/05/repair-kopitiam-speciality-electrical-tools/
https://github.com/yeokm1/repair-kopitiam-training-and-equipment
Hackware v2.0 (27 July 2016)

## Slide 2: Background
Sustainable Living Lab (SL2)
  Social Enterprise
  Aims to build a Sustainable Future through community building, technology experimentation and social innovation.
  http://www.sl2square.org/
Repair Kopitiam (RK)
  Voluntary social initiative by SL2 began in Nov 2014
  Combat the Buy-and-Throw-Away culture
  Monthly event to guide residents to repair their items
  Electrical appliances, fabrics, home improvement
  Repair Coaches and not repairmen
  http://repairkopitiam.sg/

## Slide 3: Photos

## Slide 4: Agenda
Fundamental Knowledge
Problems
Solutions

## Slide 5: Inside the 3-pin mains plug (BS1363)
Earth
Yellow/Green
Connects to appliance’s external case, protects user from electric shock
Neutral
Blue/Black
Completes the circuit to generator
Tied to ground at power distribution box to ensure stable 0V
Live
Brown/Red
Source of power
Fuse
Blows on overcurrent
Usually 13A

## Slide 6: Earth connections: Normal operation
Kettle
Mains Neutral
Earth
240V
AC ~
Mains Live
Mains Earth
Fuse

## Slide 7: Live wire touches case
Kettle
Mains Neutral
240V
AC ~
Mains Earth
Mains Live
Fuse
X
Earth

## Slide 8: What if there is no Earth wire?
Kettle
Mains Neutral
240V
AC ~
Mains Live
Fuse
Fuse does not blow due to human-body resistance
Earth

## Slide 9: Circuit Breakers
MCB
RCCB
Miniature Circuit Breakers (MCBs)
What it does?
  Breaks the circuit on overcurrent eg. short circuit
Residual Current Circuit Breaker (RCCB)
What it does? Breaks the circuit on earth fault
Cause: Current leakage via Earth wire or human electrocution
When?: Breaks when current difference between live neutral > threshold (usually 30mA)

## Slide 10: Circuit breaker arrangement
Kettle
Mains Neutral
240V
AC ~
Mains Live
Earth
Mains Earth
RCCB
MCB
Residual Current Circuit Breaker (RCCB)
What it does? Breaks the circuit on earth fault
Cause: Current leakage via Earth wire or human electrocution
When?: Breaks when current difference between live neutral > threshold (usually 30mA)
Miniature Circuit Breakers (MCBs)
What it does?
  Breaks the circuit on overcurrent eg. short circuit
Fuse

## Slide 11: Residual Current Circuit Breaker with Overcurrent Protection (RCBO)
Kettle
Mains Neutral
240V
AC ~
Mains Live
Earth
Mains Earth
RCBO
Fuse
RCBO = RCCB + MCB

## Slide 12: Problems
Safety
Inaccessible onsite breaker
Inconvenience of breaker trip

## Slide 13: Problem 1: Safety
Typical I△n = 30ma threshold for earth leakage
Balance between safety and nuisance trips
But RK always deals with high-risk faulty appliances…

## Slide 14: Problem 2: Inaccessible onsite breaker
Circuit breaker inside locked electrical room
Access to electrical room requires calling Essential Maintenance Service Unit (EMSU)
75 mins response time

## Slide 15: Problem 3: Inconvenience of breaker trip
Breaker trips affect the work of others
Eg. Those using sewing machines and welding

## Slide 16: Solution 1 for safety problem
A more sensitive circuit breaker
RCBO with I△n = 10mA sensitivity
ABB DS201 B10 A10
Installed with multi-meter to monitor line voltage/current
Ammeter helps to detect appliances which use high currents

## Slide 17: Solution 2 for inaccessible circuit breaker
Goals:
  Prevent the onsite 30mA circuit breaker from tripping
  BUT still maintain safety by tripping our 10mA RCBO
trip-10ma-rccb-only-tool modified from power strip

## Slide 18: Demo video of trip-10ma-rccb-only-tool
Open trip-10ma-rccb-only-tool.mov
https://www.youtube.com/watch?v=OAcWiW7V_oI

## Slide 19: Design of trip-10ma-rccb-only-tool
20K Ω resistor on Earth line
Rightmost socket switch as test button
Before
After

## Slide 20: Why 20K ohm resistor?
Goal: Trip our 10mA breaker and not onsite’s 30mA one
Trip margin can be 50% of rated: 15mA
So earth current must be < 15mA, we start with 14mA
Voltage (V) = Current (I) x Resistance (R)
-> R = V / I
R = 240 / 0.014 ≈ 17K Ω
But tests indicate a breaker can trip still trip due to existing earth leakage
I finally settle with 20K Ω -> 12mA of leakage.

## Slide 21: External breaker can still trip
There is an Earth-leakage via means other than the Earth wire
There is an overload in the circuit eg short circuit.
  Overload Trip sensitivity of external breaker higher than ours

## Slide 22: Solution 3 for inconvenience of breaker trip
Goals:
  Prevent even 10mA circuit breaker trips to avoid interrupting others’ work
  Bright LEDs to indicate earth leakage
anti-trip-earth-leakage-detector modified from power strip

## Slide 23: Demo video of anti-trip-earth-leakage-detector
Open anti-trip-earth-leakage-detector.mov
https://www.youtube.com/watch?v=tSpie7baYFM

## Slide 24: Design of anti-trip-earth-leakage-detector
62K Ω resistor on Earth line
Bright 600mcd LEDs to display even at low current
Rightmost socket switch as test button
Before
After

## Slide 25: Why 62K ohm resistor?
Goal: Do not even trip our 10mA breaker
Trip margin can be 50% of rated: 5mA
So earth current must be < 5mA, we start with 5mA
Voltage (V) = Current (I) x Resistance (R)
-> R = V / I
R = 240 / 0.005 ≈ 48K Ω
So resistance > 48K Ω
I finally settle with 62K Ω -> 3.87mA of leakage.

## Slide 26: Solution 4: Solution 1 + Solution 2
10mA RCBO + trip-10ma-rccb-only-tool
10ma-rcbo-and-anti-external-cb-trip

## Slide 27: Demo video of 10ma-rcbo-and-anti-external-cb-trip-with-anti-trip-earth-leakage-detector
Open 10ma-rcbo-and-anti-external-cb-trip-with-anti-trip-earth-leakage-detector.mov
https://www.youtube.com/watch?v=h-DokWP5Kic

## Slide 28: Design of Solution 4

## Slide 29: Next Repair Kopitiam
Every last Sunday of the month
10am to 3pm, Sunday 31 July 2016
Locations:
  Block 425 Jurong West Ave 1
  Block 819 Tampines Street 81
https://www.facebook.com/repairkopitiam/
FB Group on Repair Advice and queries
  Love Your Barang? Fix Your Barang! By Repair Kopitiam
  https://www.facebook.com/groups/1611578529156041/
New volunteers WELCOME!

## Slide 30: Why not an isolation transformer?
Picture from: https://cnx.org/resources/d9a067d1533f2d80b43bec5d36470711ad71b34f/Figure_24_08_08.jpg
But first what is an isolation transformer?
An isolation transformer is a transformer used to transfer electrical power from a source of alternating current (AC) power to some equipment or device while isolating the powered device from the power source, usually for safety reasons. (Wikipedia)

## Slide 31: So why not use an isolation transformer?
Eg. Carroll & Meynell, 3kVA CM3000/230 Single 13A
Heavy: 18kg each
Hides earth faults since RCCB does not trigger
Can only use on one appliance at a time
240V
AC ~
1:1
Isol.
Trf.
Kettle 1
Kettle 2
240V Primary : 240V Secondary