## Slide 1: Repair Kopitiam Circuit Breaker Training
For Repair Kopitiam Training
By: Yeo Kheng Meng (yeokm1@gmail.com)
https://github.com/yeokm1/repair-kopitiam-training-and-equipment
http://yeokhengmeng.com/2016/05/repair-kopitiam-speciality-electrical-tools/
http://yeokhengmeng.com/2017/07/repair-kopitiam-specialty-electrical-tools-part-2-short-circuit-limiter/

## Slide 2: Agenda
Knowledge Recap
Problems
Solution
Electrocution case study

## Slide 3: Inside the 3-pin mains plug (BS1363)
Earth
Yellow and Green
Connects to appliance’s external case, protects user from electric shock
Neutral
Blue
Completes the circuit to generator
Tied to ground at power distribution box to ensure stable 0V
Live
Brown
Source of power
Fuse
Blows on overcurrent
Usually 13A

## Slide 4: Earth connections: Normal operation
Kettle
Mains Neutral
Earth
230V
AC ~
Mains Live
Mains Earth
Fuse

## Slide 5: Live wire touches case
Kettle
Mains Neutral
230V
AC ~
Mains Earth
Mains Live
Fuse
X
Earth

## Slide 6: What if there is no Earth wire?
Kettle
Mains Neutral
230V
AC ~
Mains Live
Fuse
Earth

## Slide 7: But this does not happen in practice

## Slide 8: MCB + RCCB Circuit Breakers
MCB
RCCB
Miniature Circuit Breakers (MCBs)
Breaks the circuit on overcurrent eg. short circuit
Residual Current Circuit Breaker (RCCB)
What it does? Breaks the circuit on earth fault
Cause: Current leakage to Earth
When?: Breaks when current difference between
(|live| - |neutral|)> 30mA threshold

## Slide 9: Circuit breaker arrangement
Miniature Circuit Breakers (MCBs)
Breaks the circuit on overcurrent eg. short circuit
Residual Current Circuit Breaker (RCCB)
What it does? Breaks the circuit on earth fault
Cause: Current leakage to Earth
When?: Breaks when current difference between
|live – neutral|> 30mA threshold
9
Kettle
Mains Neutral
230V
AC ~
Mains Live
Earth
Mains Earth
RCCB
MCB
Fuse

## Slide 10: Residual Current Circuit Breaker with Overcurrent Protection (RCBO)
RCBO = RCCB + MCB
Kettle
Mains Neutral
230V
AC ~
Mains Live
Earth
Mains Earth
RCBO
Fuse

## Slide 11: Blackout recovery procedure
Why? Overcurrent or earth-leakage detected
Turn off every electrical device
Flip breaker to ON
Turn on ONE device at a time. If it trips again, you have found your spoilt device.
  Prioritise simple devices like lamps/ovens.
  Computers and refrigerators are sensitive to repeated power cycles.
Unplug that spoilt appliance
Flip breaker back on.

## Slide 12: Problem 1: Safety
Typical I△n = 30ma threshold for earth leakage which is still dangerous
Balance between safety and nuisance trips
But RK always deals with high-risk faulty appliances…

## Slide 13
GFCI = RCCB
https://www.quora.com/How-much-voltage-is-dangerous-for-humans/answer/Mukund-Todmal
It is not voltage but the current flowing through body will decide lethality.

## Slide 14: Problem 2: Inaccessible onsite breaker
Circuit breaker inside locked electrical room
Call Essential Maintenance Service Unit (EMSU) to unlock
30-60 mins response time

## Slide 15: Problem 3: Inconvenience of breaker trip
Breaker trips affect the work of others eg. Sewing machine

## Slide 16: Solution for RCCB earth-leakage trips
Increased safety due to more sensitive 10mA trip rating
Isolates earth trips to this device, onsite breaker RCCB does not trip
Demo video: https://www.youtube.com/watch?v=h-DokWP5Kic
Jurong
Tampines

## Slide 17: RCBO trip status + Demo
Earth trip: Switch and blue tab is down
Overload trip: Only switch is down

## Slide 18: Solution for MCB short-circuit trips
Jurong
Tampines
Isolates short-circuits to this device, onsite breaker MCB should trip lesser
Connect DOWNSTREAM to RCBO

## Slide 19
Video URL: https://www.youtube.com/watch?v=VpU6cOnxy0s
20 seconds startup time to let current measurement settle. Notice the left relay is kept off till startup is done.
Turn on a lamp: There is a 1 second delay between turning on the lamp and the second relay being turned on. Also notice the display backlight turns on and the buzzer buzzes once.
Turn off the lamp: The display backlight turns off immediately and the buzzer buzzes twice.
Repeat steps 2 and 3 for the hair dryer. Notice the motor sound is lower during the 1 second period.
Short circuit with a cable with its live and neutral pins shorted. The moment the switch is turned on, the device cuts off power to the outgoing socket. The buzzer also buzzes for a long 2 seconds. Notice the onsite MCB in the room did not trip as the device is still on.
Reset the device with just a simple button press.
Solution to prevent MCB trip (Demo)

## Slide 20: How to use it?
Make sure LCD backlight is off
Plug in appliance and turn on.
Short circuit detection mode
  After one second, limiter will be bypassed. Buzzer sounds once
  If short circuit happens, power cutoff and buzzer sounds for 3s
Turn off appliance, buzzer sounds twice and LCD backlight turns off

## Slide 21: Test for Earth Leakage without tripping
anti-trip-earth-leakage-detector
Shows blue LED on earth fault without breaker trip
  Does not interrupt the work of others
  Preserves lifespan of RCBO
Familiarise with usage instructions beforehand
Demo video: https://www.youtube.com/watch?v=tSpie7baYFM

## Slide 22: RK circuit breaker setup
Onsite socket
RK RCBO
Anti-trip-earth-leakage-detector
Short circuit limiter
Extension bar

## Slide 23: Questions before the case study?

## Slide 24: Case study: Improper heater wiring
What happened?
  In 2016, a 15-year-old boy was electrocuted while using the water heater.
Failures drawn from coroner inquiry
  Loose Earth and Neutral Wires in 13A plug
  Neutral and Earth cables fused together
  Faulty circuit breaker
  Wired 13A single-pole switch socket instead of 20A line with double-pole switch
How did the failures lead to death?
https://www.straitstimes.com/singapore/improper-heater-wiring-caused-boys-death-while-showering
https://www.straitstimes.com/singapore/circuit-breaker-could-be-a-lifesaver

## Slide 25: Failures drawn from coroner inquiry
Heater
Mains Neutral
230V
AC ~
Mains Live
Earth
Mains Earth
RCCB
MCB
Fuse
Loose Earth and Neutral Wires in 13A plug
Neutral and Earth cables fused together
Faulty circuit breaker
Wired 13A single-pole switch socket instead of 20A line double-pole switch

## Slide 26: Path of current
Heater
230V
AC ~
Mains Live
Earth
Mains Earth
Fuse
Neutral-Earth connection causes human body to be a possible return path
  If RCCB is working, it will have tripped now.
Loose Earth and Neutral wires intermittently prevent return path of current
Faulty RCCB did not trip on imbalance between Live and Neutral during shock
RCCB
MCB
Mains Neutral

## Slide 27: What should you do?
Test RCCB monthly
Check if heater needs more than 13A-rated lines
  Make sure wires can carry required current
  Circuit breaker value must match
“Electrical work, whether at home or the office, should be carried out or supervised by a Licensed Electrical Worker (LEW).
  https://www.ema.gov.sg/Hiring_Licensed_Electrical_Workers.aspx
Electricity Act: Part 82.—(1) Subject to subsection (2), no person shall —
  (a) carry out or caused to be carried out any electrical work, unless he holds a valid electrical worker licence;
  (b) advertise or otherwise holds himself out as an electrical worker, or as a licensed electrical worker, or as a person competent or qualified by any written law to perform or carry out electrical work, unless he holds a valid electrical worker licence; or
  (c) engage knowingly any person who is not a licensed electrical worker to carry out any electrical work.
  https://sso.agc.gov.sg/Act/EA2001?TransactionDate=20021129235959#pr82-
“Your flat’s electrical wiring has a limited lifespan. The estimated average lifespan of a PVC electrical cable is approximately 25 years. You are advised to replace the electrical wiring in your flat when its lifespan is over or when its condition has deteriorated.”
  https://www.hdb.gov.sg/cs/infoweb/residential/living-in-an-hdb-flat/home-maintenance/electrical-accessories-and-wiring

## Slide 28: Questions?
By: Yeo Kheng Meng (yeokm1@gmail.com)
https://github.com/yeokm1/repair-kopitiam-training-and-equipment
http://yeokhengmeng.com/2016/05/repair-kopitiam-speciality-electrical-tools/
http://yeokhengmeng.com/2017/07/repair-kopitiam-specialty-electrical-tools-part-2-short-circuit-limiter/

## Slide 29: Behaviour State 0
MCB Relay
Bypass Relay
10-ohm resistor

## Slide 30: Behaviour State 1
MCB Relay Closed
Bypass Relay Open

## Slide 31: Behaviour State 2a
Appliance connected and 1 second of no short circuit
Bypass Relay closes -> Full current
If appliance turns off, go back to State 0

## Slide 32: Behaviour State 2b
If short circuit happens, MCB relay opens
MCB relay closes only if user resets the system

## Slide 33: System weakness
Short Circuit after Resistor has been bypassed
Multiple downstream appliances

## Slide 34: Resistor Overheat Alert
70°C buzzer/blink warning
85°C function ceased till temperature < 70°C
Video URL: https://www.youtube.com/watch?v=O4qB3WehqlA
Should not happen under normal cases

## Slide 35
Mac Power Adapter
Earth pin is the circular knob
Power Adapter Extension cable with Plug Head
Silver Earth Connection is available to mate with the circular knob of power brick
Why some Macbooks have static feeling?
Power Adapter Plug Head
No Earth Connection is available