## Slide 1: Repair Kopitiam Circuit Breaker Training
By: Yeo Kheng Meng (yeokm1@gmail.com)
https://github.com/yeokm1/repair-kopitiam-training-and-equipment
http://yeokhengmeng.com/2016/05/repair-kopitiam-speciality-electrical-tools/
For Repair Kopitiam Training

## Slide 2: Inside the 3-pin mains plug (BS1363)
Earth
Yellow/Green
Connects to appliance’s external case, protects user from electric shock
Neutral
Blue/Black
Completes the circuit to generator
Tied to ground at power distribution box to ensure stable 0V
Live
Brown/Red
Source of power
Fuse
Blows on overcurrent
Usually 13A

## Slide 3: Earth connections: Normal operation
Kettle
Mains Neutral
Earth
240V
AC ~
Mains Live
Mains Earth
Fuse

## Slide 4: Live wire touches case
Kettle
Mains Neutral
240V
AC ~
Mains Earth
Mains Live
Fuse
X
Earth

## Slide 5: What if there is no Earth wire?
Kettle
Mains Neutral
240V
AC ~
Mains Live
Fuse
Fuse does not blow due to human-body resistance
Earth

## Slide 6: Circuit Breakers
MCB
RCCB
Miniature Circuit Breakers (MCBs)
What it does?
  Breaks the circuit on overcurrent eg. short circuit
Residual Current Circuit Breaker (RCCB)
What it does? Breaks the circuit on earth fault
Cause: Current leakage via Earth wire or human electrocution
When?: Breaks when current difference between live neutral > threshold (usually 30mA)

## Slide 7: Blackout recovery procedure
Why? Overcurrent or earth-leakage detected
Turn off every electrical device
Flip breaker to ON
Turn on ONE device at a time. If it trips again, you have found your spoilt device.
  Prioritise simple devices like lamps/ovens.
  Computers and refrigerators are sensitive to repeated power cycles.
Unplug that spoilt appliance
Flip breaker back on.

## Slide 8: Circuit breaker arrangement
Kettle
Mains Neutral
240V
AC ~
Mains Live
Earth
Mains Earth
RCCB
MCB
Residual Current Circuit Breaker (RCCB)
What it does? Breaks the circuit on earth fault
Cause: Current leakage via Earth wire or human electrocution
When?: Breaks when current difference between live neutral > threshold (usually 30mA)
Miniature Circuit Breakers (MCBs)
What it does?
  Breaks the circuit on overcurrent eg. short circuit
Fuse

## Slide 9: Residual Current Circuit Breaker with Overload Protection (RCBO)
Kettle
Mains Neutral
240V
AC ~
Mains Live
Earth
Mains Earth
RCBO
Fuse
RCBO = RCCB + MCB

## Slide 10: Problems
Safety
Inaccessible onsite breaker
Inconvenience of breaker trip

## Slide 11: Problem 1: Safety
Typical I△n = 30ma threshold for earth leakage
Balance between safety and nuisance trips
But RK always deals with high-risk faulty appliances…

## Slide 12: Problem 2: Inaccessible onsite breaker
Circuit breaker inside locked electrical room
Access to electrical room requires calling Essential Maintenance Service Unit (EMSU)
75 mins response time

## Slide 13: Problem 3: Inconvenience of breaker trip
Breaker trips affect the work of others
Eg. Those using sewing machines and welding

## Slide 14: Jurong Setup

## Slide 15: 10ma-rcbo-and-anti-external-cb-trip
Increased safety due to more sensitive 10mA trip rating
Isolates earth trips to this device, onsite breaker does not trip
Read instructions and test before use
Demo video: https://www.youtube.com/watch?v=h-DokWP5Kic

## Slide 16: RCBO trip status
Earth trip: Switch and blue tab is down
Overload trip: Only switch is down

## Slide 17: anti-trip-earth-leakage-detector
Shows blue LED on earth fault without breaker trip
  Does not interrupt the work of others
  Preserves lifespan of RCBO
Upstream must have 10mA RCBO
Familiarise with usage instructions beforehand
Demo video: https://www.youtube.com/watch?v=tSpie7baYFM

## Slide 18: Tampines Setup

## Slide 19: 10ma-rcbo-mcb-and-anti-external-cb-trip
Increased safety due to more sensitive 10mA trip rating
Isolates earth trips to this device, onsite breaker does not trip
Extra MCBs to increase chances of “catching” overcurrent
Read instructions and test before use

## Slide 20: Bypass B3 MCB switch
Blow margin
No blow margin
No blow margin
0A
9A
May blow
13A
15A
Sure blow margin
Blowing range of Type B: 3 – 5 times rated current
3A x (3 to 5)= 9A to 13A
13A
Fuse
Type B
3A MCB
Temporarily turn on Bypass Switch if you encounter high power appliances
How?

## Slide 21: Setup is not fool proof!
There is an Earth-leakage via means other than the Earth wire
There is an overload in the circuit eg short circuit.
  Overload Trip sensitivity of external breaker better than ours

## Slide 22: General order of diagnosis
Advise participant about warranty. Then ask what is wrong, specifically if their breaker trips
Connect to main power and try to power on
Check fuse for continuity
Dismantle part of appliance to reach the other end of power cable and test entire cable for continuity
No trip
Diagnose component by component till you find the fault or give up
ELCB trips
No Power
No Power
If “anti-trip-earth-leakage-detector” is available, use it to determine if earth fault exists. Try to locate any short to Earth wire. Dismantle appliance if needed.